## LFP
| Technology | Battery storage system (LFP Lithium-ion)
|  | 2024 | 2030 | 2040 | 2050 | 2070 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
[7 empty] | Lower | Upper | Lower | Upper |  |  | Comments:
| Energy/technical data | [11 empty] | References to be given in proper format and not as links- Done
| Generating capacity for one unit (MW) | 1-100 | [8 empty] | A | 1 | We might add a technology specific data part here as well as in DK TC - power density, etc. data - Done
| Round trip efficieincy (%AC) | 92 | [8 empty] | B | 10 | Added Power Density. Energy Density can also be added
| Round trip efficieincy (%DC) | 96 | [8 empty] | C | 10 | In note G it says lifetime can go up to 1000, but the data in the table is already 4000? - It was a typing erroror for 10000
| Energy loss duirng storage (%/day) | 0.076 | [9 empty] | 4 | Note H is for NMC, but used here for LFP? - Same Construction time assumed for NMC and LFP for this project
| Forced outage (%) | 1 | [9 empty] | 5 | Finalise and remove all the remarks - Done
| Planned outage (weeks per year) | 1.5 | [9 empty] | 5 | Various times Indian and DK tech cat are mentioned in the notes - we can just give it as a reference instead only. - Done
| Auxiliary Power Consumption (%) | 1 | [8 empty] | E | 7 | Note L mentions that this number is from a study, but which one? Is it ref 5 the Indian tech cat? Yes.
| Technical inverter lifetime (years) | 10 | [8 empty] | D | 3 | Reference 6 is for costs, but no costs are given. Reference has been corrected.
| Lifetime (battery cycles) | 4000 | [8 empty] | G | 3 | For the generating capacity we might indicate a range (see first tech cat also) - Done
| Construction time (years) | 2 | [8 empty] | H | 3
| Storage capacity (MWh) | 0.4 | [8 empty] | I | 3
| Charging efficiency (%) | 95 | [9 empty] | 5
| Depth of Discharge (%) | 70 | [8 empty] | K | 3
| Discharge time (h) | 2 | [8 empty] | L | 5
| Power Density (w/m3) | 280 | [8 empty] | M | 11
Regulation ability
| Primary load support (% per 30 seconds) | 100 | [9 empty] | 5
| Secondary load support (% per minute) | 100 | [9 empty] | 5
| Minimum load (% of full load) | 0 | [9 empty] | 5
Financial data (in 2023₹)
Capital cost
| - per MWh basis (cr. ₹/MWh) | 4.3 | [9 empty] | 9
| - per MW basis (cr. ₹/MW) | 13.6 | [9 empty] | 9
| Fixed O&M (cr. ₹/MW/year) | 0.033 | [9 empty] | 9
| Variable O&M (₹/MWh) | 42.33 | [9 empty] | 9
Notes
A | This has been taken according to name plate rating as given in reference [1]
B | Taken from LFP battery data sheet.
C | Assuming round trip effieciency (DC) to be more than round trip effieciecny (AC) by 4 percentage
D | This is according to Indian pilot project with rating 250 kWh/500kW
E | Taken from test results of PSE Utilility at glacier with 4.4 MWh capacity
G | This is according to Indian pilot project with rating 250 kWh/500kW , the life cycles for LFP can go upto 10000 under optimum conditions [8]
H | This is according to Indian pilot project with rating NMC 10MW/10MWh
I | According to LFP utilility scale commercial example
K | According to LFP pilot project example
L | This parameter has not been specified seperately in the guidelines. 2 Hrs has been considered as per the regulation abilities in India
M | Assuming that power desnity of LFP battery is approximetaly 25% less than NMC battery
References:
1 | Delta LFP based battery storage system specifications available at https://www.deltaww.com/en-us/products/Energy-Storage-Systems/LFP-Battery-System
2 | Victron energy LFP data sheet available at https://www.victronenergy.com/upload/documents/Datasheet-BMS-12-200-EN.pdf
3 | TERI and Shakti Foundation Report "Energy Storage at the Distribution Level – Technologies, Costs and Applications" available at https://shaktifoundation.in/wp content/uploads/2022/01/Energy-Storage-at-the-Distribution-Report-.pdf
5 | First Indian Technology catalogue for Energy storage available at https://cea.nic.in/wp-content/uploads/irp/2022/02/First_Indian_Technology_Catalogue_Generation_and_Storage_of_Electricity-2.pdf
6 | Bill Schweber ,"Lithium Batteries for EVs: NMC or LFP?" EE times available at https://www.eetimes.com/lithium-batteries-for-evs-go-nmc-or-lfp/#:~:text=Along%20with%20energy%20density%20figures,cells%20at%20~%24100%2FkWh.
7 | Crawford et al ,Office of scientific and technical information , US dept. of energy "Energy Storage System Consolidated Performance Test Results" https://www.osti.gov/servlets/purl/1602252
8 | Yuliya Preger et al "Degradation of Commercial Lithium-Ion Cells as a Function of Chemistry and Cycling Condition" Journal of electrochemical society DOI 10.1149/1945-7111/abae37
9 | Indian Institute of management Ahemdabad ,International study on Financing Needs for New Age Critical Clean Energy Technologies: Battery Energy Storage (BES) available at https://www.iima.ac.in/sites/default/files/2023-03/2_BES%20Report%20%2809-03-2023%29.pdf
10 | Victron energy LFP data sheet https://www.victronenergy.com/upload/documents/Datasheet-BMS-12-200-EN.pdf
11 | Danish Energy Catalogue Version 6 Available at https://ens.dk/sites/ens.dk/files/Analyser/version_06_-_technology_datasheet_for_energy_storage.xlsx

## NMC
| Technology | Battery storage system (NMC Lithium-ion)
|  | 2024 | 2030 | 2040 | 2050 | 2070 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
[7 empty] | Lower | Upper | Lower | Upper
Energy/technical data
| Generating capacity for one unit (MW) | 1-100 | [8 empty] | A | 1 | Comments: | Response to the comments
| Round trip efficieincy (%AC) | 95 | [9 empty] | 3 | We should use Indian Tech cat data rather than the Shakti data | changes made by including the Indian technology catalogue data
| Round trip efficieincy (%DC) | 91 | [9 empty] | 3 | For the generating capacity we might indicate a range (see first tech cat also) | changes made
| Energy loss duirng storage (%/day) | 0.076 | [8 empty] | B | 2 | Battery cycles here is very low and much lower than first tech cat (6000) | Changed reference to first Tech data for NMC
| Forced outage (%) | 1 | [9 empty] | 1 | How can generating capacity and storage capacity be the same when it is also specified that it is a 2h battery? | Storage Capacity is corrected as per Discharge time parameter
| Planned outage (weeks per year) | 1.5 | [9 empty] | 1 | No sources on the cost data - we can just use Indian TC data here | changes made by including the Indian technology catalogue data
| Auxiliary Power Consumption (%) | 1 | [9 empty] | 1 | Fixed O&M seems very high | Changed reference to first Tech data for NMC
| Technical inverter lifetime (years) | 16.6667 | [9 empty] | 1 | We do not have any notes at all for this about our assumptions? | Most of the data is taken from the Tata Aes 10 MW NMC pilot project and does not inlcude any particular assumptions
| Lifetime (battery cycles) | 6000 | [9 empty] | 1 | Do we need to add a category for round-trip efficiency for both AC and DC (is in DK tech cat)? | Added
| Construction time (years) | 0.86 | [9 empty] | 1 | In DK tech cat there is also a parameter called "Energy losses during storage (%/day)". Should we also add this? | Added
| Storage capacity (MWh) | 2-200 | [9 empty] | 1 | We might add a technology specific data part here as well as in DK TC - power density, etc. data | Power density parameter added
| Charging efficiency (%) | 95 | [9 empty] | 1
| Depth of Discharge (%) | 92.3333 | [9 empty] | 1
| Discharge time (h) | 2 | [9 empty] | 1
| Power density(kw/m3) | 385 | [9 empty] | 3
Regulation ability
| Primary load support (% per 30 seconds) | 100 | [9 empty] | 1
| Secondary load support (% per minute) | 100 | [9 empty] | 1
| Minimum load (% of full load) | 0 | [9 empty] | 1
Financial data (in 2023₹)
Capital cost
| - per MWh basis (cr. ₹/MWh) | 2.375 | [9 empty] | 1
| - per MW basis (cr. ₹/MW) | 6.7333 | [9 empty] | 1
| Fixed O&M (cr. ₹/MW/year) | 0.083333 | [9 empty] | 1
| Variable O&M (₹/MWh) | 500000 | [9 empty] | 1
REFERENCES
1 | First Indian Technology catalogue for Energy storage available at https://cea.nic.in/wp-content/uploads/irp/2022/02/First_Indian_Technology_Catalogue_Generation_and_Storage_of_Electricity-2.pdf
2 | Modeling the effects of state of charge and temperature on calendar capacity loss of nickel-manganese-cobalt lithium-ion batteries - ScienceDirect
3 | Danish Energy Catalogue Version 6 Available at https://ens.dk/sites/ens.dk/files/Analyser/version_06_-_technology_datasheet_for_energy_storage.xlsx
Notes
A | The pilot project in India had a capacity of 10 MW but larger rating projects are in the pipeline , hence we can consider a range
B | Here in the reference the energy loss is obtained as 2.3 % per month so obtained for per day by division with 30

## PSP - On-river
Technology
|  | 2024 | 2030 | 2040 | 2050 | 2070 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
[7 empty] | Lower | Upper | Lower | Upper
Research Data
| Energy/technical data | [11 empty] | Comments: | Response to comments
| Generating capacity for one unit (MW) | 250 | [9 empty] | 1 | References to be given in a suitable format | Appropriate changes made
| Electricity efficiency, condensation mode, gross (%) | 80.4 | [8 empty] | B | 2 | No notes for any of the assumptions? | Notes Added
| Forced outage (%) | 1.03 | [8 empty] | C | 3 | What is the source of the research data for construction time? | Reference added
| Planned outage (weeks per year) | 2.3 | [8 empty] | D | 4
| Auxiliary Power Consumption (%) | 1 | [9 empty] | 5
| Technical lifetime (years) | 50 | [9 empty] | 9
| Construction time (years) | 4.5 | [9 empty] | 8
| Storage capacity (MWh) | 4000 | [8 empty] | A | 1
| Charging efficiency (%) | 74.1 | [8 empty] | B | 2
| Discharge time (h) | 7 | [9 empty] | 7
Regulation ability
| Ramp Up Rate (% of Full Load/Minute) | 50 | [9 empty] | 9
| Ramp Down Rate (% of Full Load/Minute) | 50 | [9 empty] | 9
Primary load support (% per 30 seconds)
Secondary load support (% per minute)
Minimum load (% of full load)
Financial data (in 2023₹)
| Capital Cost (cr. ₹/MW) | 6 | [9 empty] | 9
- of which equipment (%)
- of which installation/development (%)
- of which is related to rent of land (%)
- of which is related to other costs (i.e. compensation of neighbours, etc.) (%)
| Fixed O&M (cr. ₹/MW/year) | 0.15 | [9 empty] | 9
Variable O&M (₹/MWh)
References
1 | Tehri PSH specifications by THDC available at : https://www.thdc.co.in/en/content/tehri-pumped-storage-plant
2 | CEA chief Engineer review report of the Tehri Project available at : "https://cea.nic.in/wp-content/uploads/hpm/2022/06/T_Report_Nov21_MT.pdf"
3 | CAG audit report available at : https://cag.gov.in/uploads/download_audit_report/2015/Union_Performance_Commercial_CPSE_Report_41_2015_chap_4.pdf
4 | Tae-Woo Kim et al ,"Preventive Maintenance and Forced Outages in Power Plants in Korea" https://res.mdpi.com/d_attachment/energies/energies-13-03571/article_deploy/energies-13-03571-v2.pdf
5 | IITR ,"TECHNO-ECONOMIC STUDIES FOR CAPACITY AND UNIT SIZE OF HYDRO ELECTRIC SCHEMES" available at " https://iitr.ac.in/Departments/Hydro%20and%20Renewable%20Energy%20Department/static/Modern_hydroelectric_engg/vol_1/Chapter-2_Techno-Economic_Studies_for_Capacity_and_Unit_Size_of_Hydro_Electric_Schemes.pdf
7 | SCHEDULING OF HYDRO PLANT PUMPED STORAGE SCHEME INTEGRATING RE SSP EXPERIENCE , available at : https://cea.nic.in/wp-content/uploads/2020/03/annexures_mom-psp.pdf
8 | Article on Tehri PSH project available at https://www.power-technology.com/projects/tehri-pumped-storage-plant/
9 | First Indian technology catalogue - https://cea.nic.in/wp-content/uploads/irp/2022/02/First_Indian_Technology_Catalogue_Generation_and_Storage_of_Electricity-2.pdf
Notes
A | "There are 4 units of 250 MW each in the Tehri PSP project, and the discharge time is 4 hours. Hence, the total capacity in megawatt-hours (MWh) should be 4 units * 250 MW/unit * 4 hours = 4000 MWh."
B | The overall cycle efficiency will be about 80.4% considering conventional energy generation and 74.1% considering pure pump operation
C | forced outages in NJHPS were 2736 machine hours for total of 262800 working hours , which worked out to be 1.041 per cent
D | Planned outage for maintenance (days) for Korian PSH plant[4] were 16.50 days in the year which works out as 2.35 weeks per year

## PSP - off-river
Technology
|  | 2024 | 2030 | 2040 | 2050 | 2070 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
[7 empty] | Lower | Upper | Lower | Upper
Research Data
Energy/technical data
| Generating capacity for one unit (MW) | 200 | [9 empty] | 1 | Comments:
| Electricity efficiency, condensation mode, gross (%) | 80 | [8 empty] | A | 2 | References to be given in a suitable format - Done
| Forced outage (%) | 1.031 | [8 empty] | C | 3 | I tried to follow the link for Ref 1, but could not find any of the data specified here for costs, lifetimes, etc. - Correct reference added
| Planned outage (weeks per year) | 2.3 | [8 empty] | D | 4 | No notes for any of the assumptions? - Notes Added
| Auxiliary Power Consumption (%) | 1 | [9 empty] | 5 | The % sum of capital costs does not add up to 100% - Rest is land related cost.
| Technical lifetime (years) | 40 | [9 empty] | 6
| Construction time (years) | 3 | [9 empty] | 1
| Storage capacity (MWh) | 8400 | [8 empty] | B | 1
| Charging efficiency (%) | 70 | [9 empty] | 6
| Discharge time (h) | 8 | [9 empty] | 1
Regulation ability
| Ramp Up Rate (% of Full Load/Minute) | 50 | [9 empty] | 2
| Ramp Down Rate (% of Full Load/Minute) | 50 | [9 empty] | 2
Primary load support (% per 30 seconds)
Secondary load support (% per minute)
Minimum load (% of full load)
Financial data (in 2023₹)
| Capital Cost (cr. ₹/MW) | 4.54 | [9 empty] | 1
| - of which equipment (%) | 41 | [8 empty] | E | 1
| - of which installation/development (%) | 49 | [8 empty] | F | 1
| - of which is related to rent of land (%) | 3.46 | [8 empty] | G
| - of which is related to other costs (i.e. compensation of neighbours, etc.) (%) | 2 | [9 empty] | 1
| Fixed O&M (cr. ₹/MW/year) | 0.1 | [9 empty] | 6
Variable O&M (₹/MWh)
References
1 | Greenko Report on IREP project available at : https://environmentclearance.nic.in/writereaddata/modification/Amendment/Attach_file/130820189Y14XCLVUpdatedForm1PFRandotherdocuments.pdf.pdf
2 | EERA , Pumped hydro storage factsheet available at : https://www.eera-energystorage.eu/component/attachments/?task=download&id=683:EERA_Factsheet_Pumped-Hydro-Energy-Storage
3 | CAG audit report available at : https://cag.gov.in/uploads/download_audit_report/2015/Union_Performance_Commercial_CPSE_Report_41_2015_chap_4.pdf
4 | Tae-Woo Kim et al ,"Preventive Maintenance and Forced Outages in Power Plants in Korea" https://res.mdpi.com/d_attachment/energies/energies-13-03571/article_deploy/energies-13-03571-v2.pdf
5 | IITR ,"TECHNO-ECONOMIC STUDIES FOR CAPACITY AND UNIT SIZE OF HYDRO ELECTRIC SCHEMES" available at " https://iitr.ac.in/Departments/Hydro%20and%20Renewable%20Energy%20Department/static/Modern_hydroelectric_engg/vol_1/Chapter-2_Techno-Economic_Studies_for_Capacity_and_Unit_Size_of_Hydro_Electric_Schemes.pdf
6 | First Indian Technology catalogue for Energy storage available at https://cea.nic.in/wp-content/uploads/irp/2022/02/First_Indian_Technology_Catalogue_Generation_and_Storage_of_Electricity-2.pdf
Notes
A | The reference defines the round trip efficeicncy in the range of 75-85 , here mean value of 80 is taken.
B | MWh rating=MW capacity × Discharge duration , here we have MW capacity = 1200 MW and discharge duration as 7h so it becomes 8400 MWh
C | forced outages in NJHPS were 2736 machine hours for total of 262800 working hours , which worked out to be 1.041 per cent
D | Planned outage for maintenance (days) for Korian PSH plant[4] were 16.50 days in the year which works out as 2.35 weeks per year
E | Total cost of the project is 5468.02 Cr Rs and the Cost of Power Plant Electro Mechanical Equipmen including Transmission line is 2263.68 Cr Rs
F | Cost of Civil Works is 2684 Cr Rs
G | Rest od the cost is assumed to be land acquisition and related costs

## VNR flow battery
| Technology | Vanadium Redox Flow batteries
|  | 2024 | 2030 | 2040 | 2050 | 2070 | Uncertainty (2024) |  | Uncertainty (2050) |  | Note | Ref
[7 empty] | Lower | Upper | Lower | Upper
Energy/technical data
| Application | System, power- and energy-intensive
| Generating capacity for one unit (MW) | 0.2 | [8 empty] | A | 1
| Round trip efficieincy (%AC) | 77 | [8 empty] | B | 7
| Round trip efficieincy (%DC) | 81 | [8 empty] | C | 8
| Energy loss duirng storage (%/day) | 0 | [8 empty] | D | 9 | Comments:
| Forced outage (%) | 0.5 | [9 empty] | 2 | References to be given in a suitable format - Done
| Planned outage (weeks per year) | 0 | [9 empty] | 2 | No notes for any of the assumptions? - Notes Added
| Auxiliary Power Consumption (%) | 10 | [8 empty] | E | 3 | Align more with the categories in the DK tech cat? E.g. round-trip efficiency, add breakdown of costs into energy, capacity and other? - Added
| Technical inverter lifetime (years) | 20 | [9 empty] | 6 | Ad technology specific data section also? - Added
| Lifetime (battery cycles) | 10000 | [9 empty] | 1
| Construction time (years) | 6 | [9 empty] | 5
| Storage capacity (MWh) | 1 | [9 empty] | 1
| Charging efficiency (%) | 97 | [9 empty] | 4
| Depth of Discharge (%) | 100 | [8 empty] | F | 1
| Discharge time (h) | 4 | [9 empty] | 6
| Power density (W/m3) | 2260 | [9 empty] | 9
Regulation ability
Primary load support (% per 30 seconds)
Secondary load support (% per minute)
Minimum load (% of full load)
Financial data (in 2023₹)
Capital cost
| - per MWh basis (cr. ₹/MWh) | 4.6 | [9 empty] | 7
| - per MW basis (cr. ₹/MW) | 17.5 | [9 empty] | 7
| Fixed O&M (cr. ₹/MW/year) | 0.04 | [9 empty] | 7
| Variable O&M (₹/MWh) | 40.4 | [9 empty] | 7
References
1 | Delectrik RFB200x data sheet available at https://delectrik.com/products-2/
2 | Mexico Technology catalogue for energy storage 2020 available at https://www.gob.mx/cms/uploads/attachment/file/590028/11_INFORME_D2_Technology_Catalogue_Energy_Storage_INGLES_CGMCC.pdf
3 | Henrik Bindner et al "Characterization of Vanadium Flow Battery" , National laboratory for sustainable energy available at "https://orbit.dtu.dk/files/5889861/ris-r-1753.pdf"
4 | A Karrech et al ,"Vanadium flow batteries at variable flow rates", Journal of energy storage , Vol 45 ,2022 available at "https://doi.org/10.1016/j.est.2021.103623"
5 | Andy Colthorpe , "First phase of 800MWh world biggest flow battery commissioned in China ,Energy Storage news available at https://www.energy-storage.news/first-phase-of-800mwh-world-biggest-flow-battery-commissioned-in-china/
6 | https://energystoragesolutions.com/vanadium-redox-flow-batteries/
7 | https://www.iima.ac.in/sites/default/files/2023-03/2_BES%20Report%20%2809-03-2023%29.pdf
8 | Shakti Foundation "Energy Storage at the Distribution Level – Technologies, Costs and Applications" https://shaktifoundation.in/wp content/uploads/2022/01/Energy-Storage-at-the-Distribution-Report-.pdf
9 | Danish Energy Catalogue Version 6 Available at https://ens.dk/sites/ens.dk/files/Analyser/version_06_-_technology_datasheet_for_energy_storage.xlsx
Notes
A | The generating capacity is given as 200 kW * N so for 1 unit it will be 200 KW or 0.2 MW
B | The reference mentions AC round trip efficiency of 70-85 % hence 77 is taken as mean value here
C | DC round trip effeiceincy is greater than than AC round trip efficiency and [8] mentions that DC round trip effieincy is greater than 75 hence the appropaite value is selected
D | VRFB exhinit low self discharge rates due to Chemical Stability of Vanadium Redox Couples, energy being stored in liquid electrolytes contained in separate tank,and low Crossover of Electrolytes:
E | The auxiliary power consumption of a VRFB is high due to the power required to operate the pumps and other auxiliary equipment that circulate the electrolyte solution through the battery stack
F | VRFB have high DOD due to Chemical design of electrolyte and long life cycle .